VOLUME 4.2

FINANCIAL OFFER TEMPLATES

LUMP SUM CONTRACTS

Content

4.2.1 — Introduction

4.2.2 — Summary

4.2.3 — Breakdown of the Lump-sum Price

4.2.4 — Daily work Schedule

VOLUME 4.2.1 — INTRODUCTION

1. 	General

1.1	The Breakdown of the Lump-sum Price (Volume 4.2.3) is the itemised list of prices showing the build-up of the price in a lump-sum contract. This Breakdown of the Lump-sum Price does not derogate in any way to the clause stating that, in a lump-sum contract, the total contract price remains fixed irrespective of the quantity of work actually carried out.

The amounts due will be calculated:

<For example: through the measurement of the percentage of works carried out in relation to the firm quantities of each item of the Breakdown of the Lump-sum Price and by applying that percentage to the lump-sum price of the related item>

<For example: by the tranches specified in article 49(1)(a) of the Special Conditions>.

1.2	The Detailed Breakdown of Prices (Volume 4.2.5) is the list which contains the basic costs, net costs and mark-ups, from which each price on the Breakdown of the Lump-sum Price and on the Daywork Schedule results. The Detailed Breakdown of Prices does not derogate in any way to the clause according to which, in a lump-sum contract, the total contract price remains fixed irrespective of the quantities of work actually carried out.

The Detailed Breakdown of Prices provides the coefficients for applying the price revision formula referred to in Article 48.2 of the Special Conditions and can provide the basis for valuation of additional work ordered referred to in Article 37.5 of the General Conditions.

1.3	Provisional sums for use when works are to be executed on a daywork basis (Volume 4.2.4) can only be executed by administrative order of the Supervisor, in accordance with the terms of the Contract.

2.	Specific to Volumes 4.2.2, 4.2.3 and 4.2.4

2.1	The item description given in the Breakdown of the Lump-sum Price in no way limits the Contractor’s obligations under the Contract to provide all the works described elsewhere.

2.2	The prices of the Breakdown of the Lump-sum Price include all incidental and contingent expenses and all risks necessary to construct, complete and maintain all works in accordance with the Contract. Unless separate items are provided in the Breakdown of the Lump-sum Price, prices include all costs involved in the various items of the Breakdown.

2.3	The prices do not include taxes and fiscal duties, as exoneration is explicitly given for the Contract. Non-exonerated taxes and fiscal duties are, apart from those stated separately in the financial offer templates, covered in the Lump–sum Price of the Contract and in the prices of the Breakdown of the Lump-sum Price and of the Daywork Schedule.

2.4	The Unit prices in Volumes 4.2.3 and 4.2.4 are obtained by multiplying the Net cost of Volume 4.2.5 - Table D, on the one hand, with the coefficient K, on the other hand.

The coefficient K represents the proportions between the Site costs (Fc) of Volume 4.2.5 - Table E and the Total net costs (Ps) and between the General costs (Fg) of Volume 4.2.5 - Table F and the Contract price (Pv): K = (1+A)/(1-B) whereby

A= Fc/Ps

B =Fg/Pv

VOLUME 4.2.2 — SUMMARY

| Description | Amount EUR |
| --- | --- |
| Total of lump-sum price |  |
| Total of Dayworks — Provisional sum |  |
| TOTAL PRICE |  |

VOLUME 4.2.3 — BREAKDOWN OF THE LUMP-SUM PRICE

A. Installation of a stabile fire extinguishing system

| Item | Description |  | Lump-sum price in EUR |
| --- | --- | --- | --- |
| I | SPECIFICATION FOR SPRAY EQUIPMENT |  |  |
| 1.1 | EQUIPMENT AND DEVICES |  |  |
| 1. | WET ALARM SPRINKLER STATION set with valve DN150 PN10, retard chamber, pressure switch, alarm bell, impurity strainer, manometers, necessary taps, counter flanges, seals, screws, nuts and elastic washers. Total 1 set. |  |  |
| 2. | FLOW METER DN80 PN16 RANGING FROM 0-636m3/h Set of flanges, counter flanges, seals, screws, nuts and washer. Total 1 set. |  |  |
| 3. | FLANGE STAINER set of counter flanges, seals, screws ,nuts and elastic washers. DN150 PN16. Total 1 set. |  |  |
| 4. | Backflow prevention device, with flanges, hydraulic,with attestation. It is calculated and paid per one installed piece, set of flanges, counter flanges, seals, screws, nuts and elastic washers. DN150 PN16. Total 1 set. |  |  |
| 5. | NON-RETURN CLAPPER INSTALLED BETWEEN FLANGES Set of flanges, counter flanges, seals, screws,nuts and elastic washers. DN150 PN16. Total 1 set. |  |  |
| 6. | Sluice valves with flange, SRPS M.C5.670 2A Set of counter flanges, seals, screws,nuts and elastic washers. DN150 PN16. Total 8 sets. DN100 PN16. Total 3 sets. |  |  |
| 7. | Micro switch providing information on valve position (open/partially closed). Total 3 pcs. |  |  |
| 8. | Drainage valve. DN40 PN16. Total 1 pc. DN20 PN16. Total 3 pcs. |  |  |
| 9. | Drainage set. Galvanized pipes DN50, galvanized pipes DN25, galvanized fittings, hopper for sprinkler valve, hopper for alarm bell. Carried to the nearest drain. Total 1 set. |  |  |
| 10. | VALVE FOR TESTING AND DRAINAGE AT THE ENDS OF THE MAIN RINGS. DN50 PN16. Total 9 sets. |  |  |
| 11. | Manometer Ø100mm, with manometer type and compensation pipe R1/2", ranging 0-16bar. Total 2 pcs. |  |  |
| 12. | Flow indicator with imerssion feather, shaft collar for fixing on the pipe, elektrocontacts and a regulation switch DN100 PN16. Total 4 sets. |  |  |
| 13. | FLOW INDICATORS TESTING SET, K=80 set composed of nipples for testing with a factor K=30, ball valve 3/4" manometer ranging from 0-16bar 1/2" in accordance with VDS. Total 4 sets. |  |  |
| 14. | STEEL THREADED NIPPLE R1/2“ WITHOUT SEAM SRPS M.B6.306. Total 94 pcs. |  |  |
| 15. | SPRINKLER HEAD HANGING, type „QUICK RESPONSE“, 1/2”; K= 80, t=68°C similar to TY 3231. Total 94 pcs. |  |  |
| 16. | SPRINKLER HEAD HANGING, SPARE part, type „QUICK RESPONSE“, 1/2”; K= 80, t=68°C. Total 24 pcs. |  |  |
| 17. | Cabinet for spare heads, Capacity12 sprinkler heads. Total 2 pcs. |  |  |
| 18. | KEY FOR HEADS ASSEMBLY G 1/2". Total 5 pcs. |  |  |
| 19. | Purchase, transport and installation of flexible chrome pipes 1/2" for connecting sprinkler and pipe network in a lowered ceiling . Average length of the connection is 60 cm. Flexible pipes for operating pressure 10 bars. At both ends, each connection has union flat joint 1/2" with thread, whereas in order to attach the sprinkler rosettes and heads to the lowered ceiling, there is a metal washer and a spring. Calculations per peace of connection. Total 94 pcs. |  |  |
| 20. | Purchase, transport and installation of a cabinet, made of stainless steel, with stable fire extinguishing couplings with caps, couplings type "B" (2x2 1/2") with drain DN100. Calculation per set delivered and installed on the façade of the cabinet. Total 1 set. |  |  |
| 21. | Electric heater with work and limit thermostat for temperature maintenance in the sprinkler station, capacity of 9KW. The heater has wall holder and all necessary equipment for smooth and safe operation. Total 1 set. |  |  |
|  | Total |  |  |

| Item | Description |  | Lump-sum price in EUR |
| --- | --- | --- | --- |
| 2.1 | PIPE NETWORK AND ARMATURE |  |  |
| 1. | Steel seamless pipes, according to SRPS EN 10220:2005 WITHOUT NIPPLES, the following dimensions: DN150 (Ø165.1x4.5mm). Total 40m. DN100 (Ø114.3x3.6mm). Total 150m. DN50 (Ø60.3x2.9mm). Total 13m. DN32 (Ø42.4x2.6mm). Total 35m. DN25 (Ø33.7x2.6mm). Total 220m. DN20 (Ø26.9x2.3mm). Total 12m. |  |  |
| 2. | Cast steel fittings 90°, R=1.5D, SRPS M.B6.821, the following dimensions: DN150 (Ø165.1x4.5mm). Total 10 pcs. DN100 (Ø114.3x3.6mm). Total 15 pcs. DN50 (Ø60.3x2.9mm). Total 2 pcs. DN32 (Ø42.4x2.6mm). Total 1 pcs. DN25 (Ø33.7x2.6mm). Total 2 pcs. |  |  |
| 3. | Purchase, transport and installation of a set of various steel fittings, reduction, elbows, pipe tees, backings, hard points, flanges and all other elements for sprinkler network. Carriers are fixed for the reinforced concrete structure and steel construction. Price also includes steel rawl plugs, screws, rods and and clamps. Carriers capacity: -pipes to DN50 - 200 kg, -pipes from DN50 to DN100 - 350 kg, -pipes from DN100 to DN150 - 500 kg. Calcullation per set 50%. 50% of position 1 and 2 amount is envisaged. |  |  |
| 4. | ADDITIONAL MATERIAL for welding, electordes, wire, welding gas, reducing pieces and the like. Total 1 lump sum. |  |  |
| 5. | Purchase, transport and installation of numerous steel holders and carriers for sprinkler network pipes. Calculation per kg of carriers with external elements. Total 600kg. |  |  |
| 6. | Cleaning pipes and backings from rust and dirt and double minimization of corrosion by protective anti-corrosion paint. Total 130m². |  |  |
| 7. | Painting pipes and backings with final paint (RAL 9001). Only visible parts of pipe network will be painted. Total 130m². |  |  |
|  | Total |  |  |

| Item | Description |  | Lump-sum price in EUR |
| --- | --- | --- | --- |
| 3.1 | PREPARATORY-FINAL WORKS |  |  |
| 1. | Development of instructions for operating and maintaining as well as submission to the investor. Total 1 set. |  |  |
| 2. | Developing as-built design and submission to the investor. The project will be developed in four copies, with all necessary certificates and decisions. Total 1 set. |  |  |
| 3. | Testing a stable system for water spray and network, performing functional check of each zone separately. Minutes shall be took upon testing. It is necessary to submit certificates on technical and functional conditions of the equipment and materials incorporated. Attestation has to be performed by the company verified for the activity, which owns appropriate liscence. Total 1 set. |  |  |
| 4 | Posting notices and warning notes. Total 1 set. |  |  |
| 5. | Other preparatory-final works with transport of materials and tools, exploring the site and documentation, protecting the site and delivery of installation to the investor upon work completion. Total 1 set. |  |  |
|  | Total |  |  |

| Item | Description |  | Lump-sum price in EUR |
| --- | --- | --- | --- |
|  | RECAPITULATION |  |  |
| 1.1 | EQUIPMENT AND DEVICES |  |  |
| 2.1 | PIPE NETWORK AND ARMATURE |  |  |
| 3.1 | PREPARATORY-FINAL WORKS |  |  |
|  | Total |  |  |

B. Smoke and heat exhaust ventilation system

| Item | Description |  | Lump-sum price in EUR |
| --- | --- | --- | --- |
|  | Smoke and heat exhaust ventilation system (purchase, delivery and installation are necessary) |  |  |
| 1. | Cnetrifugal roof ventilator, the features: L=18800 m³/h, Δp=50 Pa, N=2,2 kW, n=700 minˉ¹, Declaration of the manufacturer according to SRPS EN 12101-3 standard. Total 1 set. |  |  |
| 2. | Smoke damper, dimensions 1120 x 800 mm, L=600 mm the following technical features:: - housing PPKmade of galvanized steel sheet , 1,50 mm thick and flange thread 30 mm. - Elctric actuator with return spring and end contacts,with cables 6x0,75 mm2 and 2x0,75 mm2, length 1 m. - Signalization of open and closed postition. - Fire resistance120 min. - Declaration of the manufacturer according to SRPS EN 12101-8 standard, - Cable terminals from electric actuator driver PPK made of fire resistant material. Total 1 set. |  |  |
| 3. | Regulation electric drive damper, dimensions 1185 x 900mm. Total 1 pc. |  |  |
| 4. | Smoke and heat exhaust ducts made of galvanized steel sheet 2mm thick, according to the graphic documentation. Method of installation, connecting duct parts and fittings, and manner of installing according to the technical conditions, a set of connectors and seals as well as supporting and hanging material according to SRPS EN 1366-9 standard. Weigth of channels, profiles, backing, sealss and screws. Total 350kg. |  |  |
| 5. | Final preparatory works, testing and trials regarding installation regulation. Total 1 lump sum. |  |  |
|  | Total |  |  |

C. Heating, Ventilation and Air Conditioning

| Item | Description |  | Lump-sum price in EUR |
| --- | --- | --- | --- |
| 1 | Purchase, delivery and installation of heaters, with electronic thermostat, switch for on / off and connection cable length of 1.5 m and DIN plug. Also with low temperature heaters and mount, with built-in protection IP 2,4 the following characteristic: Power: 400 W. Total 5 units. Power: 600 W. Total 5 units. Power: 800 W. Total 3 units. Power: 1000 W. Total 3 units. Power: 1250 W. Total 7 units. Power: 1500 W. Total 2 units. Power: 2000 W. Total 4 units. Power: 500 W. Total 3 units. Power: 750 W. Total 3 units. |  |  |
|  | EQUIPMENT FOR AIR PREPARATION AND DISTRIBUTION |  |  |
| 2 | Purchase, delivery and installation of the air chamber, with DR+FB+HV+VU+DI+EG+IP of the following elements: Revolutions per minute of electric motor n=1355 mm-1 Power of electrical motor P=1.5 kW Available head H=575 Pa Air flow rate V= 4000 m3/h DR-regulation damper FB-coarse filter section HV-cooler VU-ventilator user DI-diffuser EG-electric heater IP-output terminal Additional equipment for automatic control. Total 1 set. |  |  |
| 3 | Purchase, delivery and installation of the alluminium vent dampers, a set with a flow regulator for air insertion, dimensions:: 930 x 620 mm. Total 1 set. |  |  |
| 4 | Purchase, delivery and installation of elastic jute strings or similar for installation between ducts and air chamber, dimensions: 910 x 630 x 300 mm. Total 2 sets. |  |  |
| 5 | Design and installation of ventilation ducts for insertion and extraction of air. Ducts will be made of galvanized sheet, thickness according to the technical regulations for such works. Calculation is carried out per kg of the installed material, where carriers, holders, flanges, connectros and seals are included. The price includes minimazing and painting flanges and duct supporting and hanging elements with previous corrosion removal. Total 950 kg. |  |  |
| 6 | Purchase, delivery and installation of ceiling diffusers. Total 2 pcs |  |  |
| 7 | Purchase, delivery and installation of overpressure ventilation dampers dimensions 1185 x 900mm. Total 2 pcs |  |  |
| 8 | Purchase, delivery and installation of fire resistant damper with thermal, manual and remote activation with solenoid, dimensions: 500 x 500mm. Total 1 pc 630 x 630mm Total 1 pc |  |  |
|  | FINAL PREPARATORY WORKS |  |  |
| 1 | Final preparatory works include: - project analysis before works commencement; - digging in walls; - internal transport; - contact with the supervising authority; - testing installation on a hydraulic pressure; - installation regulation and activation; - collecting attesting documents and other administration activities, 5% of all above mentioned works is paid. Total 5%. |  |  |
|  | Total |  |  |

D. STAGE LIGHTING AND FIRE PROTECTION CURTAIN – SCC

| Item | Description |  | Lump-sum price in EUR |
| --- | --- | --- | --- |
| D1 | STAGE LIGHTING SYSTEM |  |  |
| 1.1 | Stage spotlights |  |  |
| 1. | Delivery and installation of the complete frensel lens spotlight (textured), wide, adjustable beam of "soft" light with edges in range from 130 to 590 made of extruded aluminium. Within the spotlight, one halogen light source is installed, rated power of 1.0 kW, rated voltage 230V/50 Hz, temperature 3200 ºK and light bulb base GX9.5. There is also a set of additional equipment: a protective lens net, a metal frame for filters, a four sided clapper, a threaded silicone cable 3 x 1.5 mm2 minimal length 2.0 m with CEE connector, a hanging hook on pipes Ø 65 mm and a safety cable.. Total 3 pcs. |  |  |
| 2. | Delivery and installation of the complete spotlight with plano-convex fully transparent collecting lens, wide, adjustable beam of "hard" light, with very prominent edges in range of 100 to 650 made of extruded aluminium.Within the spotlight, one halogen light source is installed, rated power of 1.0 kW, rated voltage 230V/50 Hz, temperature 3200 ºK and light bulb base GX9.5. There is also a set of additional equipment: protective lens net, metal frame for filters, threaded silicone cable 3 x 1.5 mm2 minimal length 2.0 m with CEE connector, hanging hook on pipes Ø 65 mm and a safety cable. Total 2 pcs. |  |  |
| 3. | Delivery and installation of the complete frensel lens spotlight (textured), wide, adjustable beam of "soft" light with edges in range from 120 to 610 made of extruded aluminium. Within the spotlight, one halogen light source is installed, rated power of 2.0 kW, rated voltage 230V/50 Hz, temperature 3200 ºK and light bulb base GX16. There is also a set of additional equipment: a protective lens net, a metal frame for filters, a four sided clapper, a threaded silicone cable 3 x 1.5 mm2 minimal length 2.0 m with CEE connector, a hanging hook on pipes Ø 65 mm and a safety cable. Total 2 pcs. |  |  |
| 4 | Delivery and installation of the complete spotlight with plano-convex lens, wide, adjustable beam of "hard" light, in range of 50 to 650 made of extruded aluminium. Within the spotlight, one halogen light source is installed, rated power of 2.0 kW, rated voltage 230V/50 Hz, temperature 3200 ºK and light bulb base GX16. There is also a set of additional equipment: protective lens net, metal frame for filters, four sided clapper, threaded silicone cable 3 x 1.5 mm2 minimal length 2.0 m with CEE connector, hanging hook on pipes Ø 65 mm and a safety cable. Total 7 pcs. |  |  |
| 5. | Delivery and installation by collecting complete, wide beam, diffuse, asymetric spotlights of "soft" light, wide beam for stage lighting, equpped with a protective net, and a four-sided frame for glass filters, CAD/PF/ACV with a hook A20 and a safety cable, with halogen light source, rated power 1.0 kW, rated voltage 230V, 50 Hz, temperature 3200 K, with the base R7S and a thread silicone cable 3 x 2.5 mm2 length of l=2.0m. Total 4 pcs. |  |  |
| 1.2 | Regulation of stage lighting |  |  |
| 1 | Delivery and installation of a manual table for regulation of stage lighting.Features: - 24 channels of configuration with 24 regulators configurated as channels, submaster or playback - MIDI IN/OUT connector - 2 DMX512/1990 terminal on XLR-5F connector - power supply 90-260V, 47/63Hz with automatic detection. Total 1 pc. |  |  |
| 2 | Delivery and installation of a digital dimmer unit for installation of the Rack The output power of the dimmer unit is 6x3 kW with DMX512/1990 input over a connector XLR5 with galvanic insullation. On the front panel of the dimmer, there is a keypad with LED display for programming and quick access to all functions, with a possibility of adjusting 10 dimmer curves, which can be individually selected for each dimmer cable, with constant storage of all programmed data. Dimmer power supply is 230V/400V,star, 3NPE (TN-S), 50/60 Hz. Within the dimmer, there is a low-noise ventilator for efficient cooling, controlled by a microproccesor with automatic stop of the ventilator and automatic protection from excessive temperature and gradual reduction of the dimmer exit to the output. Individual protection of each dimmer MCB/1P (standard), protection of circuit 400V voltage. Total 1 pc. |  |  |
| 3 | Training and certificates - certificates for the delivered equipment , - Manual for operation and maintenance of the stage lighting equipment, - training of beneficiaries. Total 1 set. |  |  |
| 1.3 | Electrical installations of stage lighting system |  |  |
| 1 | Perforated cable trays Cable trays are delivered and installed plasticized in black matte colour, with set of caps and necessary installation tools: - PNK200. Total 4m. - PNK100. Total 12m. - PNK50. Total 12m. |  |  |
| 2 | Cables Delivery and installation of cables intended for power supply of the stage lighting system. Cables are placed in cable trays: - kabl N2XH-J 3x2,5mm2. Total 468m. - kabl LIHCH 2x0,5mm2. Total 50m. |  |  |
| 3 | Wall sockets Delivery and installation of industrial sockets 16A 3p with visibly a marked dimmer number. Sockets are installed on the wall at the side spotlight carriers. Total 19 sets. |  |  |
| 4 | MDC of stage lighting. Total 1 set. |  |  |
| 5 | Certificates and testing electrical installations Testing stage lighting installations, issuing appropriate certificates and delivery of certificates for entire electrical equipment installed. Total 1 lump sum. |  |  |
|  | Total |  |  |

| Item | Description |  | Lump-sum price in EUR |
| --- | --- | --- | --- |
| D2 | STAGE MECHANICS SYSTEM |  |  |
| 2.1 | Stage nechanics devices |  |  |
|  | Delivery and installation of the following stage mechanics elements: |  |  |
| 1 | EMRC - Motorized light hoist Features of motorized light hoist with mobile drive train: * load capacity: 150kg * length and type of support: 5,5m, Al "Ω" profil * working stroke: 6m * speed: 0,09m/s * drive train: 0,75kW * pivot point: 4 * number of trolleys with brakes: 5kom * number and type of connector: 5x16A dim * number and type of connector: 1 set XLR5pin m/f * related electrical installations: set * cable tray: segmented Al pantograph * additional locksmith structures: console, racks ... Total 1 pc. |  |  |
| 2 | BNR - Spotlight side girder Features: * length and type: pipe Ø48mm, L=1,5m * spotlight girder “elbow” Total 2 pcs. |  |  |
| 3 | HNR - spotlight horizontal girder Features * length and type: pipeØ48mm, L=8m. Total 2 pcs. |  |  |
| 4 | Training and certificates - certificates for the delivered equipment , - Manual for operation and maintenance of the stage mechanics equipment, - training of beneficiaries. Total 1 set. |  |  |
| 2.2 | Electrical installation of the stage mechanics system |  |  |
| 1 | RO-SM Stage mechanics distribution cabinet RO-SM in intended for providing power and controlling with one electric motor drive of the stage mechnics and is located in the appropriate place above the audience. The cabinet is a product by a stage mechanics devices manufacturer, which contains complete equipment neccesary for supply, protection and management of electric motor drive. Total 1 set. |  |  |
| 2 | Cables :Delivery and installation of cables intended for power supply of the stage mechanics system. Cables are placed in cable trays: * cable N2XH-J 5x1,5mm2. Total 50m. * cable N2XK 4x25mm2. Total 25m. *cableN2XK-J 1x16mm2. Total 25m. * cableN2XH-J 5x2,5mm2. Total 20m. |  |  |
| 3 | Certificates and testing electrical installations Testing stage mechanics installations, issuing appropriate certificates and delivery of certificates for entire electrical equipment installed. Total 1 set. |  |  |
| 4 | As-built project. Development and delivery of as-built project for the stage lighting and mechanics. Total 1 set. |  |  |
|  | Total |  |  |

| Item | Description |  | Lump-sum price in EUR |
| --- | --- | --- | --- |
| D3 | AUTOMATIC FIRE PROTECTION CURTAIN |  |  |
| 3.1 | Fire protection curtain with necessary control panel and related equipment |  |  |
| 1 | Delivery and installation of the fire protection curtain elements and necessary automatics: Fire protection curtain is fire resistant 90-120 min. It is made of fibre glass fabrics, especially tested for fire resistance - it holds fire up to 1100 ° C for 90-120 minutes. Threaded plate is 70mm thick and made of galvanized steel. Vertical pipes are galvanized 110 mm wide. Speed of curtain closure is 7m/min. Upon fire occurrence, the curtain is automatically closed, even with supply interruption, thus activating optic and sound alarm. On the lower part of the curtain, there is additional contact safety rubber. Dimensions of a panel 300x250mm and it enables all door functions up to 4 hours after power outage. On the panel, there is the command UP-STOP-DOWN button integrated. Power supply of the curtain is 220/230V/50 X3/20 A. Electrical connector 3 x 2,5mm. The curtain dimensions are 11250mm x 4500mm. The fire resistant curtain has to be delivered with appropriate certificates from the manufacturer. Total 1 pcs. |  |  |
|  | Total |  |  |

RECAPITULATION

|  |  |  | Lump-sum price in EUR |
| --- | --- | --- | --- |
| D1 | STAGE LIGHTING SYSTEM |  |  |
|  | 1 Stage spotlights |  |  |
|  | 2 Stage lighting regulation |  |  |
|  | 3 Electrical installations of stage lighting system |  |  |
| D2 | STAGE MECHNICS SYSTEM |  |  |
|  | 1 Stage mechanics devices |  |  |
|  | 2 Electrical installations of the stage mechanics system |  |  |
| D3 | AUTOMATIC FIRE PROTECTION CURTAIN |  |  |
|  | 1 Fire protection curtain with necessary control panel and related equipment |  |  |
|  | Total |  |  |

|  | SUMMARY |  | Lump-sum price in EUR |
| --- | --- | --- | --- |
|  | OF WORKS ON THE FIRE EXTINGUISHING INSTALLATION AND MECHANICAL ENGEENERING INSTALLATION ON FACILITY OF SURDULICA CULTURAL CENTRE |  |  |
| A | Installation of a stabile fire extinguishing system |  |  |
| B | Smoke and heat exhaust ventilation system |  |  |
| C | Heating, Ventilation and Air Conditioning |  |  |
| D | Stage lighting and fire protection curtain |  |  |
|  | TOTAL |  |  |

VOLUME 4.2.4 — DAYWORK SCHEDULE

| Item | Description | Unit | Unit price | Estimated quantities | Provisional sum [EUR] [local currency] |
| --- | --- | --- | --- | --- | --- |
|  | Labour |  |  |  |  |
|  | Materials |  |  |  |  |
|  | Equipment |  |  |  |  |
|  | Total dayworks provisional sum |  |  |  |  |