Project N CB007.1.11.349: Creating preconditions for better accessibility to touristic attractions in Pantelej and Lom by improving the touristic infrastructure and increasing the number of tourists;...

# VOLUME 3

# TECHNICAL SPECIFICATIONS

Contract title: Repairs and renovation of the Multifunctional Cultural and Tourist Center and the adjoining infrastructure

Project No CB007.1.11.349:  Creating preconditions for better accessibility to touristic attractions in Pantelej and Lom by improving the touristic infrastructure and increasing the number of tourists; Priority Axis: 1.Tourism; Specific Objective: 1.1 Tourist Attractiveness; Type of project: Investment, financed by the European Union, in accordance with the rules of Interreg – IPA CBC Bulgaria – Serbia Programme

Location: Municipality of Lom, Republic of Bulgaria

SECTION 1: PARTICULAR TECHNICAL SPECIFICATION

## 1. Background and purpose of the Project

The project envisages a complete renovation of the building of the Multifunctional Cultural and Tourist Center in the town Lom and adjacent land to her – a road with parking, sidewalks and construction site recreation with access to the building. The building has two floors and a basement, Built 300 m 2. The repair includes first and second floor area of 470 m 2 and includes: thermal insulation of external walls; repair roof gutters, gutters, chimneys; replacement of wooden windows; replacement of interior doors; new electrical, plumbing and HVAC systems; internal repair of the premises. The surrounding area will be shaped as an area for access and recreation area, which will be situated: 5 parking cars for visitors to the center; wood and metal benches - 16 pcs .; playground with benches and flower round; wooden gazebo; flower beds; walkways to connect to the main street; waste bins; metal table tennis outdoor games; lighting.

The aim of the project is a complete renovation of the building of the Multifunctional Cultural and Tourist Center in the town  Lom and adjacent land to her and turning it into an information center. The rehabilitated infrastrucutre to the new Center in Lom will make it an attracting center of culture, history and tourism.

2. Current situation

Subject of this project is the building of the Youth Centre, which is located in the town of Lom in private Regulated plot of land X kv.284 identifier is 44238.500.148. Act on Municipal property № 1574 / 10.09.2009.It was built in 1962 as a two-storey with basement. Served with an internal and an external staircase. The roof is flat with insulation on concrete slab. The substructure is solid concrete skeleton. It consists of inter-floor slabs, beams and columns. The walls are bearing with surrounding and insulating function. The outer walls are 30 cm and internal 25cm. They are met by single solid bricks of lime solution, framed with monolithic reinforced belts and columns. Brick walls act as washers and absorb horizontal forces of wind and earthquake. Missing insulation.

General structural condition of the building is good. Over the years, made minor repairs, without prejudice to the supporting structure.

When made detailed view would not have detected any damage to the reinforced concrete structure. The brick walls are also free of cracks and other damage. Bearing elements are in good condition - No visible deformation, deflections of the floor structures, cracks in the vertical load-bearing elements. Construction of the building missing file and is committed capture space to design a project for repair. An attentive view of the place of the current state of construction.

Provided repairs

Planned repairs will improve the working conditions in the community center will preserve the building and ensuring the functioning and years ahead.

In the upcoming repair

will make external insulation of the walls.

will make a new roof insulation.

will replace wooden windows.

will execute a new power, plant.

will perform new plumbing.

will execute a new heating and ventilation system

will perform internal repair of premises and replacement of doors.

This repair is not cut through holes in the bearing elements / plates columns, beams / and do not implement new structural elements.

3. Scope and description of the construction works

3.1.Part Architecture

Basis for design:

The project was made in relation to investment intentions for renovation of the building and in case of a sketch by the Chief Architect of the Municipality of Lom as well as adjoining terrain, road parking, sidewalks and playground for recreation with access to the building. The terrain and building municipality owned, destined "for public use".

Regulated land property is located between the main street and neighborhood destined for low rise residential construction. The building of the Youth Centre was built in 1962. The building is on two floors, built with monolithic construction. There is a basement, where are located service premises that are not used and are not subject to the project. Built up area is made according to the architectural survey and document property.

The exterior walls of the building are made of brick masonry 3O cm with appropriate external and internal plaster. Areas under the windows from the outside and on the board of the roof sheathing has pine paneling in poor condition. During the inspection of the building was found to have areas with damaged and fallen cement-sand plaster. The building has made partial repairs especially in rooms that are used but overall the building needs major renovation.

Project objective:

Made an architectural shooting of the building with identifying problems in walls, floors, ceilings, roof, staircase access to the building. The project envisages replacement of flooring in all rooms except mosaic foyer and staircase. Will make a new processing walls and laying the latex painted, replacement of all interior doors MDF and aluminum, new windows PVC, suspended ceilings, replacement of equipment and bathroom on the first floor and three new, one of which is for people with disabilities. It will be replaced with a new electrical system. Will repair the roof, gutters, gutters, chimneys. Will be installed metal barred windows on the first floor, which will be painted in white.

Presented are details for the implementation of measures part construction concerning the thermal insulation of walls, plinth above the terrain of the basement and insulation plate over all the rooms on the second floor.

The balcony on the second level on the request of the investor will be repaired with detail as usable roof (see the detail).

The floor will be repaired everywhere replacing existing flooring except corridors and staircase where only provides cleaning of the existing mosaic flooring.

Thermal insulation on the walls will be same for the facade of the first, second floors and the ground floor.

Thermal insulation on the 1st and 2nd floor is 10 cm EPS finish with mineral plaster color white RAL 2009 and applied in detail.

When laying gypsum cardboard some of heights will be specified in place, the place of windows on the facade, so that the ceiling is not in contrast with them and considering a minimum height of 2.70 sm.

Accessible architectural entrance:

People with disabilities and mothers with baby strollers will have easy access to the lobby, which is currently at 0.60 cm height. To overcome this doorstep is expected to make a ramp with a slope of 5% and a minimum width of 120 cm. With a protective metal railing in detail.

Part: Planting and utilities:

According to the task of repairing subject and the surrounding area as a zone for access and recreation area, which are organized into two parts with functional relation. Currently, this part will build components for recreation, but infrastructure elements, sewer manholes, - pavement, asphalt road. Almost no trees. In this area are situated:

- parking for 5 cars;

- 16 pieces of wooden benches with metal elements;

- circular area with benches and flower with a diameter of 4 meters;

- square wooden gazebo;

- flower areas;

- Walkway contact The central street;

- trash bins;

- metal table tennis outdoor games;

- lighting.

Car park has a capacity of providing parking for visitors to the center. Provided Walkway are rated to handle visitors to the basic entrance from the street, which is from the south. The design provides example landscaping consistent with park furniture and Ordinance No. 1 Maintaining hygiene during operation to provide mobile trash bins of solid polymer concrete blocks and removable metal bins - a total of 75 units.

3.2. Part Electrical

3.2.1 INDOOR PLANTS

LIGHTING INSTALLATION

Lighting installation is calculated on the basis of normal illumination according to EN 124641 for lighting systems.

The type of lighting fixtures is selected depending on the purpose of the premises, and the models will be chosen by the Contracting Authority.

The lighting system will be filled with LED luminaires, thereby realize savings of electricity energy. Instalation will be filled with cable NYY 3 x 1.5 and 4 x 1.5 mm2 laid in corrugated pipes u 16 mm hidden under plaster and over ceiling. The fourth core will be used for earthing of the lighting and the three cores will be used for serial command of the lighting system.

The lighting will be controlled by switches mounted 1.0 meters from the floor

For the site is provided evacuation lighting, which will be powered by bus duty, according to the requirements of Regulation Iz-/29.10.2009 1971, Prom. SG.96 of 4 December 2009., corr. SG. Issue 17 of March 2, 2010. amend. SG. No. 101 of December 28, 2010. amend, and supplemented. SG. 75 of 27 August 2013. suppl. and amend. SG issue 69 and No. 89 of 2014. Evacuation lighting will be filled with LED lamps with pictograms with autonomous power supply with the possibility of light at least 1.5 hours. The projected lighting fixtures for lighting evacuation provide the required illumination of 1 lx in the escape paths to safely leave the site in stopping the main power supply.

Fixtures for lighting will be installed on the walls to a height of 1.8 meters above the floor and exits.

The same is connected directly to the fuse and off key, operates in continuous recharging and when the power automatically turns on.

Installation of lighting will be filled with cable NYY 3x1.5 mm2 laid in corrugated u 16 mm pipes hidden under plaster. The use of bridge and single core conductor in installations for evacuation and emergency lighting is forrbiden.

Area lighting will be powered by MDB. Trunk lines will be filled with cable NYY 3 x 4 mm2 laid in earth trench 0.8 / 0.4 m on a sand pad in green areas and under Alain cables will be pulled in PVC pipes u 50 mm laid in a trench 0.8 / 0.4 m.

Local light is designed with LED lighting (LED). They will be mounted on a steel tubular poles submersible to three meters height 2.5 m total size fl 08 / 60 complete with junction box with park lighting with LED 30 W - vision of belaying cleats and lantern given for the pain consistent with the designer before buying. They are liked and approved by the Contracting Authority.

Deviations from the main conductor will be implemented by deflection box fuse 4 A built-in ladder.

From boxes to lighting fixtures in bars will be downloaded cable NYY 3 x 1.5 mm2.

From excavation to the cable box will be protected with PVC pipes u 29 mm.

Diverting boxes are mounted inside the pillars and serve for electrical protection and distribution.

Lighting conditions of the garden will be controlled by a photocell on the facade of the building.

In preference to the Contracting Authority is technically possible to command and clock.

3.2.2.POWER INSTALLATION

The power installation is calculated based on capacity set of appliances in equipment. All consumers have a plug-in connection with the exception of the the boiler, which is commanded by a boiler panel.

All contacts will be a ground terminal and will be powered by a cable NYY 3 x 2.5 mm2 and 3x4 mm2 laid in corrugated pipes u 16 mm hidden under plaster. Contacts will be installed 0.4 meters above the floor.

3.2.3. Current installations

There is a low voltage box whose size will be coordinated with local operators. It will be featured active Internet device, amplifier for TV and telephone slug. From light current box type cable FTP Category 5e 4 twisted pairs in corrugated pipe 23 mm u hidden under plaster will be powered phone jacks - RJ-1l. They will be installed 0.4 meters above the floor. It is envisaged cabling. For the purpose of the light current box to places of computers will be pulled cable type FTP Category 5e 4 twisted pairs in corrugated pipe 23 mm u. Cables will end rosette type RJ -45/2 ha hidden installation.

There are outlets for cable TV. They will meet with 75 ohm coaxial cable laid in corrugated pipes u 23 mm hidden, but the power will be executed by a local operator.

Weak systems have a clearance of 10 cm from high voltage and 15 cm between them to avoid interference.

3.2.4. Lightning protection system

The building under Regulation 4/2010 is in category III lightning protection zone with type "A".

Lightning protection system will be implemented by 1 number lightning rod outrun effect ERICO-SI 4 Oi mounted on a mast height of 2.0 meters and secured to the building structure (chimney). When constructive solution to strengthen the mast to provide the necessary stability of the mast and perspiration of atmospheric influences / storms /. The same may be decided by electrical engineers - constructor.

Principles of use, technical requirements and parameters of the terminals with faster action is indicated by the factory and according to French standard NFC17-102.

Lightning will be filled with extruded aluminum wire AlMgSi 0,5 u 10 mm laid on mounting holders. Vertical outlets will be filled with extruded aluminum wire AlMgSi 0,5 u 10 mm laid hidden in the facade / gutters can and fasteners for gutter /. Grounding will be deep grounding round solid steel u 17.2 mm copper-clad length of 1.5 meters set in 2 pieces. The control terminals to the grounding poles will be installed 40/4 mm galvanized strip protected in heat shrink tubing to minimize foot tensions. The transient impedance to be less than 20 ohms.

The relation between aluminum and steel elements will be carried out by bimetallic compounds. 1,2 m from ground level will be filled detachable attachment to control resistance. The control connector will be installed in a metal box with a lockable door marked "Lightning" sagl.chl.127, paragraph 2 of Regulation 4/2010, the Enactment of lightning protection systems in accordance with Article 171 under par. 1 and 3 of Regulation 4/2010 d document an act of performed construction works, drawn up by the contractor and the designer and contain at least the results of measuring the resistance of the grounding (s) and conclusion of conformity with the project.

Art. 172. After the construction lightning protection systems are adopted and put into operation under the Bulgarian Law of Spatial Planning.

3.2.5. Safety measures

MDB will be grounded with galvanized rail 40/4 mm laid hidden in the ground floor and a framework for deeper grounding of round solid steel u 17.2 mm copper-clad length of 1.5 meters set in 2 pieces.

Light installation will be performed with single-phase three-wire lines for consumers and for three-phase petprovodni according Art. 1753 of Ordinance №3 device of electrical installations and power lines, SG br.90 / 13.10.2004 and 91 /14.10.2004 effective from 15.01.2005. All contacts and housings of luminaires will be grounded with additional wire power cables.

Pursuant to the requirements of Art. 1789, 1796 of Ordinance №3 in the electrical panel of the circuits for all consumers, with the exception of the circuits for lighting will be fitted with automatic fuses combined overcurrent and earth leakage protection with instant shutdown and tripping current 30 mA, whose dimension is reflected in the explanatory table of power, dashboard. Defective current protections must comply with Bulgarian State Standard EN 61008-1 /2-1 and Bulgarian State Standard EN 61009-1 /2-1.

3.2.6. FIRE SAFETY CONCERNING EELECTRICAL PART

- Class building functional fire danger is F2, subclass classes F2.1.

- All electrical installations and equipment in the facility will be implemented according to the requirements of Art. 237 for first "Normal fire danger".

- All electrical materials / switches, junction boxes, consoles / will be met by products of reaction to fire A2 or at least "B".

- In terms of electrical safety electrical installations are provided under a scheme TN-S- function of the protective and neutral conductor are separated for the whole scheme.

- Electrical panel in the building is equipped with circuit breakers for protection against overload and short circuit.

- In the control cabinet are provided for RCDs of 30 mA for protection of electrical installations against rupturing.

- The cables will be protected in corrugated pipe made of products belonging to reaction to fire at least "B".

- All electrical switches, sockets, junction boxes and fixtures should be mounted safety base - class reaction to fire A2.

- MDB is not installed in a separate room because of imput current is less than 250A

- All rooms are secured with artificial lighting according to BS EN 12-464-1 for lighting systems.

- Openings through which cables pass in adjacent rooms will be sealed with noncombustible building material - lime and cement solution or another class of reaction A2.

- In eventual fires in electrical facility not allowed putting it off before the electricity be turned off.

- Technical specifications of used cables	:

- Classification of reaction of the electric cables are -V1.

Cable MCT type is manufactured according to Bulgarian State Standart 16291-85. Designed installation in hidden rooms and outdoor installation outdoors, trenches, cable channels, tunnels, shafts and operate at temperatures from -30 o C to +50 o C. Impact Resistant flame BDS IEC 332-1, which classifies it in class V1sa. Correspondence between European classes of reaction and national groups of combustibility insulation of electrical cables - according to EN 60332-1-2 - Test method BDS IEC 332-3 / 82 Category A.

- All products and components of electrical installations and to assemble with relevant specifications and declarations according to Bulgarian State Standart EN.

3.2.7. Environmental Protection

During the execution of electrical installations not to upset the balance of the environment and not destroy protected by law species and unique natural areas. During the process of electrical equipment and installations do not produce environmentally harmful electromagnetic radiation and are not separated noxious and poisonous gases.

3.2.8. Noise and vibrations

In the accompanying documentation (manuals for maintenance) work equipment shall specify technical data about the levels of noise and vibration and additional measures to reduce their harmful effects.

Electrical equipment and installations, which will be installed at the site do not create noise and vibration outside the rules whose limits are regulated in Decree № 6 of 26 June 2006 on noise indicators.

3.3. PART Heating and ventilation

3.3.1.Heating - air conditioning

The building is existing two-storey, which will be reconstructed for needs of multifunctional cultural and tourist center - the town of Lorn.

The site is located within the town. Lorn third climatic zone with the following characteristics: Winter - external calculation temperature - -17 ° C; number of heating days - 180 NW wind direction, speed of wind - 4.4 m.

In the characteristics of the building and at the request of the investor heating during the cold winter season and cooling during the hot summer will be performed by inverter air conditioners and electric wall heaters ..

Heat load of 43613,58 W and cold load of 34 394 W total for the building will be covered by three types of air conditioning systems KC1, KC2, SPC and one type of heater. Air conditioning system КС 1 will be installed in the room № 107 -Office staff. The system consists of indoor high wall mounting (mounted at a height of 2.20 m + floor of the room) and outdoor unit mounted on the facade of the building elevation + 0.45 m. The connection between the two bodies is effected by technological pipes Cul0h0.8mm 12x0.8mm. To insulate pipes with pipe insulation K-flex. Internal body drains through drainage pipe 20 mm. Technological pipelines and drainage pipe is collected in a single bundle and wrapped in bandage tape. The pipe bundle runs along the inside wall of the room, descends to the level of the unit and is displayed in the area of the room the unit. To respect displacement between internal and external body at least 1.5 meters strengthen internal body wall through dowels. The outdoor unit is placed on consoles.

The characteristic of the climate system is as follows;

TYPE: Inverter

Power output (cooling): 0.60-2.65-3.20 kW power output (heating): 0.80-2.80-3.60 kW Power consumption (cooling):

0.89kW Power consumption (heating): 0.90 kW EER (energy

efficiency ratio, cooling): 2.98 COP (odds, transformation heating): 3.11 Energy class (cooling / heating): A +/ A Noise levels -Interior, exterior body: 28-51 dB Dimensions

(indoor): 27.5 84.5X18 cm.

Dimensions (outdoor unit): 54X77.6X32 cm.

Weight (indoor): 9 kg. Weight (outdoor unit): 28 kg. Refrigerant R410

KC 2 air conditioning system will be installed in the room № 101 Office personnel 103 - scene 105 - stairs, 106 exhibition and information hall, 202 - and 204 stairs - Domestic office. The system consists of indoor high wall mounting (mounted at a height of 2.20 m + floor of the room) and outdoor unit mounted on the facade of the building elevation + 0.45 m for systems serving the first floor level and elevation + 3.40 m systems serving the second floor level. The relationship between the two bodies is through technological pipes Sil2h0.8mm and his 19 h0.8mm. To insulate pipes with pipe insulation K flex. Internal body otvodnava through drainage pipe 20 mm u. Technological pipelines and drainage pipe is collected in a single bundle and wrapped in bandage tape. The pipe bundle runs along the inside wall of the room, descends to the level of the unit and is displayed in the area of the room the unit. To respect displacement between internal and external body at least 1.5 meters, strengthen internal body wall through dowels. The outdoor unit is placed on consoles. The characteristic of the climate system is as follows:

TYPE: Inverter

Power output (cooling): 1,26-5,20-6,00 kW power output

(heating):	1,12-5,65-6,86kW8 Power consumption

(cooling): 1,67 kW Consumption ( heating): 1,75 EER (energy efficiency ratio, cooling): 3.11 COP (coefficient, transformation heating): 23.3 Energy Class (cooling / heating): A +/ A Noise levels -Interior, outdoor unit: 35 -56 dB Dimensions (indoor): 29.8 94X20 cm.

Dimensions (outdoor unit): 70X95,5X39,6 cm.

Weight (indoor): 12 kg. Weight (outdoor unit): 45 kg.

Refrigerant R410

Air conditioning system KC 3 will be installed in the room № 102 visitors lounge, 201 - Tourist Information Center, 203 - Youth Cultural Center. The system consists of indoor column for floor mounting and outdoor unit mounted on the facade of the building elevation + 0.45 m for sistemito serving first floor level and elevation + 3.40 m for systems serving the second floor level. The relationship between the two bodies is through technological pipes Sil2h0.8mm and his 19 h0.8mm. To insulate pipes with pipe insulation K flex. Internal body otvodnava through drainage pipe 20 mm u. Technological pipelines and drainage pipe is collected in a single bundle and wrapped in bandage tape. The pipe bundle runs along the inside wall of the room, descends to the level of the unit and is displayed in the area of the room the unit. To respect displacement between internal and external body at least 1.5 meters, strengthen internal body wall through dowels. The outdoor unit is placed on consoles. The characteristic of the climate system is as follows:

TYPE: inverter

Power output (cooling): 1,80-9,80 kW power output (heating):2,00-9,00kW Power

consumption (cooling):2,20kW Power

consumption (heating): 2,40 kW EER ( energy efficiency ratio, cooling): 3.21 COP (coefficient, transformation heating): 3.61 Energy class (cooling / heating): A +/ A Noise levels -Interior,

exterior body: 50-55 dB Dimensions (indoor)n

180H 35X55 cm.0

Dimensions (outdoor unit): 94X124X36 cm.,

Weight (indoor): 58 kg. Weight (outdoor unit): 104 kg.

Refrigerant R410

FROM 1 - electric heater for wall mounting. Radiators are sized 600/25/35 mm - installed in offices 104 and 205. Strengthening is done by plugs at a height of 1.60 from the floor and at the locations indicated on the line. № 1 and №2.

El. Power supply to all air conditioning systems is subject to the project - part Electrical.

Consumed heat - heating bodies are calculated on the basis of the calculated heat consumed for each room. Consumed heat is heat loss through the surrounding surfaces and losses from infiltration through joints in windows and doors. In the calculations take into account the size and burning characteristics of the surrounding surfaces- walls, floors, ceilings. Also :

- temperature difference At, At = tn-tBH- Ata

- correction temperature difference Ata - reported by handbook HVAC -1 part / table - 8.2

- factor heavenly direction Zo reported by handbook HVAC -1 part table

- 8.1

- factor breathability and reported by handbook HVAC -1 part table - 8.4

- Characteristics of the room P reported by handbook HVAC -1 part table - 8.5

- Characteristics of Building C reported by handbook HVAC - I part table - 8.6 8.7 i'tablitsa a calculation of the wind in the region of location of the building is 4.4 m / sec.

- Corrective factor breathability Ka reported by handbook HVAC -1 part table - 8.9

- Corrective ventilation Kv factor reported by handbook HVAC -1 part 'table - 8:10

- Corrective factor floors of the building Ke reported by handbook HVAC -1 part table - 8.8

The calculation of heat losses reflected in Annex 1 of the explanatory memorandum of the Techical project

Cooling load - The radiators are selected so as to cover needs for space cooling in the hot season according to the cooling load calculations

The calculation of heat losses is reflected in Annex 2 to the explanatory memorandum of the Techical project. Calculations are made for indoor temperature + 26 ° C, the presence of 5 people in room 101 and 107 in 50 people per room 102 and 30 for others.

After construction of the plant and installation of air conditioning systems to perform edenichni tests and 72 hour effective sample. For samples to be drawn protocols.

The installations are equipped with instructions for installation and operation. Also be accompanied by a certificate of conformity.

3.3.2. Labor safety and hygiene technique is developed in accordance to: - techno - economic task

- ORDINANCE № 15 of 28 July 2005. technical rules and standards for design, construction and operation of facilities for the generation, transmission and distribution of heat

- BDS 14776-87 "Protection of Labour. Production microclimate standards for temperature, relative humidity, speed of air movement and heat radiation."

- BDS 7033-68 "Noise. General"

- BDS 1478-78 "Noise. Production levels and noise. "

- BDS 10705-71 "machines and equipment. Safety, hygiene and ergonomics, General. "

- BSS 9869-72 "platform and staircase of machinery and equipment. Requirement of the safety."

- BDS 11018-75 "Signs of labor safety and fire protection."

- BDS 12.4.004-78 "Occupational safety. PPE. Terms and definitions. Qualification. General."

- Rules of technical operation of energy users, DI Technique

1980.

- Rules for work safety at construction works - D02.001 M-vonaSA 1981.

- Ordinance №7 / 1999. minimum requirements for safe and healthy working conditions in the workplace and use of work equipment.

- Law on health and safety Gazette br.27 / 1997.

Based on those regulations, declarations of conformity and technical documentation accompanying the equipment by the manufacturer shall be drawn up instructions for installation and operation to ensure safe working conditions, safe from accidents, accidents and fires.

A / Safety instructions for building installations.

Works on construction of the facility to be carried out by competent persons authorized.

Work to be done under appropriate weather conditions.

Be strictly design schemes and guidelines.

Employees are provided with personal protective equipment and clothing, and specialized according to the requirements of Article 10 p. 1,2,3 from HSCWA.

Workers object to be instructed about the specifics of the types of work and precautions to prevent accidents and injuries.

Responsibility for failure to comply with labor legislation Safety wear RTD specialists on site.

During installation and - commissioning are not allowed outsiders to reach the construction site.

In case of accident or fire to act according to the instructions on fire safety

The rooms are equipped with fire fighting equipment under Decree № lz- 1971/2009.

Working Group to be equipped with a stocked pharmacy as required.

During installation works were banned - smoking, use of open flame and use of electricity. Facilities with inadequate level of protection.

B / Indication of operational safety

Commissioning after it successfully carried out samples of density, strength and effective 72 hour sample and the proper preparation protocol entered with results ..

Proper operation involves constant monitoring of the facility, power lines, power. Power. Check the condition of the insulation on the hull of the vessel, as well as - heat pipes. Check throughput and functionality of the shut-off and regulating valves.

Fire safety - object represents an existing public building of two floors with an area 300 m2 characteristics of the object relative to the requirements of Annex №9- Articles 122, al.Z of Ordinance № 15 of 28 July 2005. technical rules and standards for design, construction and operation of facilities for the generation, transmission and distribution of thermal energy not necessitating an internal smoke and heat ducts.

To ensure fire safety in the construction and operation of the site to carry out these measures.

1.To power off. Supply of all equipment in the event of fire.

2. Grounding system installation should be T-NS, the entire plant to be developed by a separate protective conductor PE.

3. In tray to provide circuit breakers, provide protection from injury by el. Current on contact with live parts or metal no live parts normally we are under stress but may fall under such a breach of the bodies provided insolation. The heaters First fully meet the requirements of Article 142 and Article 144 of Decree № lh-1971/2009.

The requirements for fire safety are part of the installation and operation of the facility provided by the manufacturer.

Emergency Activities - Possible technical failures and processes are: Breakthrough in technological pipelines of air conditioning in which can occur leakage of Freon R 410a, damage to the mechanical part of the equipment or compressor system - where can rip metal piece of equipment and to strike on the body of shipboard equipment.Action in the event of accidents are:

. 1.	Stop the operation of the facility

- Disconnect electric power supply

- Drainage of residual fluids

- Limiting access of unqualified personnel in the area of the accident

- Take emergency measures first aid to victims and call "ambulance" if necessary.

- Troubleshooting under the guidance of competent technical staff. When removing the emergency efforts to maintain unchanged the facts and situation in which it will carry out investigation and analysis of the emergence and.

Environmental protection. Provided inverter air conditioning systems do not emit harmful pollutants. Analysis of the amount of gases subjeet-of project Energy

3.4.Part: Water Supply and Sewerage

3.4.1 Water supply

For water supply of the site with domestic water will be used existing water diversion from water supply network of Lom. In the building on the first floor are divided into three new toilets, which will build new water installations. Designed to replace abstracted fixtures and fittings for cold water to all water abstraction devices in the building on the first and second floors, according to the architectural design.

Cold water pipelines supplying water abstraction devices in the building will be made of polypropylene pipes. The water supply network is designed to meet dug in the walls, such as those of external walls will be installed with insulation type "Mirelon", to prevent freezing. Cold water supplay pipe network is designed with a polypropylene tubes RSH0 with diameters in accordance with the sizing calculations.

Hot water supplay pipe network in the new toilets will be provided with electricity. Boiler with volume V = 50 1. Capacity and N = 2 kW.

Hot water toilets sinks, which replaced the valves will be provided with electric heaters. Heaters mounted toilets sinks.

All horizontal branches to make upward slope not less than 0,005 to abstracted utensils.

Fire insurance will benefit external body near the building.

a) Sizing water quantity

The water quantity is determined by the Decree № 4 / 17.05.2005 for the design, construction and operation of building water and sewerage systems, (NEW-issue 53/2005). Dimensioning seconds maximum water quantity Qmax/s for general plumbing sections with more than one tap water abstraction in buildings with a purpose is defined as:

Q max/s = 5Qe s. * Z s., wherein:

Qe s is specific sizing flow equivalent abstracted crane, which is

adopted 0.2 1 / sec.

Z s - parameter seconds probability, which is recorded in Annex we №7 by onds probability / P s / sizing section.

Second possibility of abstraction of water abstraction cranes P sec / accordance respectively for the common cold water / is determined by the formula:

Qh maks.ch. x M uch

P s =	,	wherein:

720 x Ea build.

Qh maks.ch. water supply is the maximum hourly rate of water cars - tion, respectively for the common cold water / in 1. / hour, according t.Z of Annex №4.

M - the total number of water consumers to the sizing section. Second possibility of abstraction of water abstraction cranes in common areas / P £ л s respectively for common hot and cold water is defined as:

£ / Ea crp.i x P sec /

P s Y, i =	,	wherein:

£ Ea crp.i

£ Ea build, the total number of equivalent abstracted cranes / respectively common hot and cold water in part of the building to use i.

Water supply norm of Annex №2 and №3 to article 18 paragraph 1 and 2:

Administrative buildings/employee - 12 1 / day, 4 1 / h

Visitors 	4 1 / day. 0.3 1 / h.

WATER LEVELS

Table 1 equivalent continuous A number of devices for complex-Ea vol. Mixer outfits sink	4	x 0.5 = 2.0

Flushing cistern: 3 x 0,5 = 1.5

X

Ea vol. = 3,5 £ {Q max } 2x4 +

20x0,3

Q = 5x0.2x0.212 = 0.21 1/sec.

For Q. = 0,21 1 / s. choose polypropylene pipes for cold water 10 0 C, power instruments with a diameter of f25 / 2.5 mm PPR with J = 0,365 m / s km and V = 0,6 m / sec.

TEST MEASUREMENT AND ACCEPTANCE OF PLUMBING.

After finishing the installation of plumbing tested working pressure plus 5 atm.,

But not more than 10 atm. Before the test conduit trya BVA be purged. The test lasts 15 min., During which the pressure should not drop more than 1 atm. Before adopting plumbing must be put in trial operation for at least three days (72 hours) CLOSE Rennie utility points and flushed as described below sanitary requirements. First wash water pipe to remove dirt and precipitate - characteristics that are adhering to the walls of the equipment and pipes. Then disinfected with chlorine solution containing 20-40 mg. of active chlorine (chlorinated lime) 1 l.water.Chlorine solution is kept for at least 24 hours in the pipes, after which the installation is washed.

3.4.2.Sewerage system.

For disposal of waste water from the new sanitary at fight in the building on the first floor designed new internal sewerage system with new vertical branch pipes FI 10 PVC.

The horizontal branches are designed to be built into the walls and floor slab elevation + 0.60 diameters d 110 PVC for toilet seat and u 50 sinks for PVC and PS.

The vertical branch will be discharged into existing neighboring site sewerage system.

Both of them to install manholes (see drawings).

Vertical ventilation branch will be performed with vacuum protective valve 100 mounted in the ceiling plate. The drainage of roof gutters with externally.

When repair is provided for replacement of the existing sanitation in fight and fittings of the first and second floors.

For those newly designed replacement sanitary appliances - sinks and toilets flushing plates - monoblock provided appropriate soft links u and 40 u 100 mm.

Dimensioning sewerage installations:

The waste water quantity of projected sewerage installation for the building is determined according to BS EN 12056-2 formula:

Qww = k £ л DU 1 / s, where:

Qww - waste water discharge, 1s;

k - coefficient of simultaneity;

£ DU - the sum of specific amounts of water from the individual

sanitary utensils, 1 / s.

Coefficient of simultaneity according to frequency of use sanitary instruments in Table 1.1 with intermittent use eg. Receptions and offices is K= 0.5.

Specific quantities of water for sanitary appliances in a system according to BS 12056-2 IV ottabl.1.2. They are:

- toilet washbasin 4 pcs. * 0.3 = 1.2

- toilet with flushing cistern 3 pcs.* 2.0 = 6.0

- floor drain DN 50 3 pcs.*0.6 =1.8

£ DU = 9.0

Dimensioning waste water quantity for the building:

Qww = 0.5 1 / 9.0 = 1.50 1 / sec.

Wastewater quantities of the building will be carried out by existing sewage as drains is unconfined.

The location of the projected replacement sewerage installation, as well as lengths, diameters, gradients, elevation, and other data are shown in the drawings of the project.

After completion of the sewerage system to test the tightness of the same even when the pipes are in the open position. The pipelines are wor Jatte filled with water for 24 chasa.Sled making it the samples are drawn acts rezultatite. With acceptance of the sewerage system will be checked:

- whether mounted installation meets the project and the requirements of Regulation № 4 of17.06.2005for the design, construction and operation of building water and sewerage systems.

- correctness pipeline inclination, elevation, strengthening their security and that of equipment, performance of the network, fittings and sanitary utensils.

- The maximum period of implementation of construction works should be 10 months from the date of the giving access to the Site.

- SECTION 2: GENERAL REQUIREMENTS

The Technical Specification is an integral part of the Tender Documentation /TD/ together with the provisions of the Contract, approved Investment design, the detailed design drawings, and the other contract documents. The Specification specifies and further develops the requirements for the implementation of the construction works under the Contract. Implementation of construction and assembly work must be consistent with all relevant execution of specific types of works legal and regulatory framework, technical rules and regulations and applicable standards following sequence and technology of the performance of different types of works in different parts of the site.

1.	STANDARDS

All materials and equipment shall meet the following technical specifications:

- Bulgarian standards transposing European or international standards, or equivalent;

- European technical approvals (with or without guidance);

If the technical specifications under item 1 or 2 do not exist, building materials should meet recognized national technical specifications.

Where the technical specifications cannot be defined in the top row, including where they do not exist, have not been published or are not enforced, they are determined by:

- Bulgarian standards transposing European or international standards, or equivalent;

- Bulgarian standards or equivalent;

In case that there are no published standards apply Bulgarian technical approvals and regulations for the design, implementation and supervision of works or individual construction works.

The materials which are used must correspond to the requirements of the standardized documents asset in Bulgarian State Standards Act.

If the Contractor should wish to supply material or execute work to an alternative national standard or international specification he shall give full details of his proposal in writing to the Supervisor.

2.	CONTROL OF WORKS

The Contracting Authority will provide a consultant who will supervise construction with investment functions, according to Art. 166, par. 1, item 1 of the Bulgarian Law on Spatial Planning. The Contracting Authority and / or supervisor may at any time inspect the work, control technology performance and issue instructions to remove the defects, according to the specified technology and method of implementation. If found serious defects, errors and low quality performance, the Contracting Authority shall notify the Contractor that breached the contract and should stop to work. The Contractor shall always provide access to the construction site of the authorized representatives of the Contracting Authority and the Supervisor.

2.1	Contractor's equipment

The Contractor shall furnish equipment which will be efficient and appropriate to secure a satisfactory quality of work and a rate of progress which will insure the completion of the Works within the time stipulated in the Tender. If at any time such equipment appears to be inefficient, inappropriate or insufficient for securing the quality of work required or for the rate of progress, the Supervisor may be entitled to order the Contractor to increase the efficiency, change the character or hire additional equipment, and the Contractor shall conform to such order.

2.2 Protection of existing structures and utilities

The Contractor shall assume full responsibility for the protection of all buildings, structures and roads existing in the area of the construction site, public or private, whether or not they are shown on the drawings.

When starting the contract to be invited all companies and institutions exploiting underground lines and facilities, specifying the exact location of existing underground lines/facilities and in their vicinity excavation should be carried out very carefully and in places where necessary, manually.

The Contractor has to pay special attention to avoid any damages on any protected areas if any.

Any damage resulting from the Contractor's operations shall be repaired at his expense.

2.3	Requirements regarding the provision of safe and healthy working conditions. Plan for Safety and Health

During the execution of construction works Contractor shall comply with the requirements of Ordinance № 2 of 2004 on minimum requirements for health and safety in the course of construction works, as well as all other applicable regulations and standards for safety and hygiene, industrial and fire safety during construction and operation of such sites, and also to ensure the safety of all persons who are on site.

The Contractor shall comply with the approved by the Contracting Authority and the competent authority a plan for safety and health for construction.

2.4	Approval of sources, materials and plants

Materials and plants incorporated must originate in any eligible source country as defined in of IPA Cross-border programme. For these purposes, ‘origin’ means the place where the goods are mined, grown, produced or manufactured and/or from which services are provided. The origin of the goods must be determined according to the EU Customs Code or the applicable international agreement. Material that originates from sources, which are not approved by the Supervisor, cannot be used for Works.

Approval of a source does not mean that all material in the source is approved. The Contractor has to ascertain by continuous control check measurements that only material which complies with the requirements specified in the various clauses of these specifications will be used for the Works.

2.5	 Requirements regarding environmental protection

In the execution of construction works contractor must confine its action within the construction site.

After completion of construction works the Contractor shall reimburse the construction site by the project for development and park arrangement - to withdraw all their machinery and unused materials and leave the site clean of debris and completely finished.

The Contractor shall clear way and remove from the site any wreckage, rubbish and temporary works, which are no longer required.

2.8	Responsibility of the Contractor

Approvals from the Supervisor do not relieve the Contractor from his obligations or responsibilities under the Contract.

3.	ADMINISTRATIVE SPECIFICATIONS

3.1 Implementation Programme

Implementation programme for delivery of works shall be prepared consistent with the duration of the project’s implementation and the works activities implementation. The programme shall be presented in a format which includes a bar chart of all the major activities. No later than five working days after the end of each month, the Contractor shall submit an updated programme to the Supervisor. This shall show, as a minimum:

- progress made during the past month, compared with planned progress

- activities planned for the next month.

3.2 Progress meetings

The Contractor shall agree with the Supervisor and the Contracting Authority for dates for regular progress meetings. These meetings shall normally be held monthly, no later than 10 working days after the completion of each month.

3.3 Quality assurance

The Contractor shall institute a quality assurance system to demonstrate compliance with the requirements of this contract. The system shall be in accordance with the details stated in the Contract. The Supervisor shall be entitled to audit any aspects of the system.

4.	IMPLEMENTATION OF THE WORKS

4.1	Materials

All Materials supplied to perform the Permanent Works under the contract shall be new products. Second-hand Materials will not be accepted.

Supply of all materials and equipment required for the execution of construction - assembly work according to the approved investment project is the responsibility of the Contractor. Any change to the approved design must be coordinated and approved the Contracting Authority.

All materials that would be used in the construction must be accompanied by relevant certificates of origin and quality, instructions for use and a statement certifying the compliance of each of the nested construction products with the essential requirements for building works, in accordance with the Law on technical requirements for products and by-laws to it.

The Tender drawings constitute the drawings issued for construction/ installation/ execution.

4.2	Testing

Reliable shall be only the type and amount of tests performed in conformity with the prescription of this Technical specification, except when this right is granted to the Contracting Authority.

Tests and the measurements of the performed construction works should be carried out by certified laboratories and shall be certified by protocols. The Contracting Authority may require additional tests when the results obtained are uncertain.

Beside the tests specified in this Specification, the Contracting Authority may require additional tests to establish possible hidden omissions and effects. Costs for these tests shall be entirely at the Contractor’s expense if such defects are confirmed.

4.3	Inspection and measurement of works

In the process of construction and assembly works must be compose all the necessary documents and records provided for in Ordinance № 3 from 31.07.2003 for preparation of documents and reports during construction.

The Contracting Authority may at any time inspect the quality and measure the amount of works performed. If this cannot be done with the Contractor’s assistance, a deadline shall be fixed for hiring external specialists. In this case, the expenses shall be paid by the Contractor.

5.	PREPARATORY WORKS

Before starting the works the Contractor has to perform some preparatory works at the site.

5.1	Boards and signs

The Contractor shall mount and maintain in good condition a board with the name of the project and the financing institution.

5.2 Setting out the site

The Contractor shall in co-operation with the Contracting Authority set out the total site to be used for construction.

5.3 Temporary facilities

The Contractor shall effects all expenditure for establishing, operation and removal of temporary facilities if such are needed for the good performance of the Contract. All needs for establishing such facility shall be duly justified.

5.4 General supply facilities

- Sanitary Arrangements

The Contractor shall provide for and maintain temporary sanitary facilities on the site for the use of all persons connected with the Works. The Contractor shall keep the facilities in a clean and sanitary condition, and shall post notices and take such precautions as may be necessary to keep the site clean.

- Water supply

The Contractor shall provide for and maintain an adequate supply of potable water for his use. The water supply shall be used for construction purposes and for consumption in the temporary facilities.

- Power supply

All electrical power required by the Contractor shall be provided by him at his own expense. The Contractor prior to taking-over of the Works shall remove all temporary installations if it is not agreed upon that the Contracting Authority takes over the installations.

IMPORTANT:

All works must be implemented in accordance with investment design and corresponding standards.

In case that in investment design - explanatory notes, bills of quantities, drawings, specifications, and everywhere in the documentation for tendering are set specific brand/mark, model, type, standard materials and products to be considered that whereas and equivalent.

The Contracting Authority does not require specific make, model, type, standard materials and products that will be in the works as long as you comply with the specifications of the designers and the essential requirements for building works.